## Final BOQ
UPGRADATION OF INFRASTRUCTURAL FACILITIES IN IGIDR, GOREGAON.
Quotation for Supply, Installation & Commissioning of AC VRV System (Indoor & Outdoor Unit) Work at Guest House Conference. (Phase-3), in the campus.
QUOTED AMOUNT (WITH GST)
SR. NO. | DESCRIPTION | Unit | Qty. | Rate | Amount (A) | GST % | GST Amount (B) | With GST Total Amount (A+B)
Part A - Supply
[ A ] | Outdoor units of VRV system
Supply of Compact Air Cooled type outdoor units of VRV system having ALL inverter compressor, condenser coil fabricated from Seamless Copper tube & Plate type Al. Fins of Multi Row, Axial Flow, upward throw condenser fan, Condenser fan - motor unit, insulated refrigeration piping, power / control wiring, and earthing, external wiring between Indoor & Outdoor units.
Each Outdoor units with High Pressure switch, Fan driver overload protector, Over current relay, Inverter Overload Protector & Fusible Plug. The unit shall be suitable for 415 ± 10 % volts, 50 Hz, 3 phase AC supply, and IP 55 protection.
1 | 12 HP OUTDOOR UNIT CARRIER MAKE | Nos. | 1
2 | INDOOR UNITS OF VRF
a | 2.4TR Cassette (3hp) | Nos. | 2
b | 3.2 TR Cassette (4hp) | Nos. | 2
c | Refrigerant Y / T Joints | Nos. | 6
TOTAL FOR SUPPLY AMOUNT (A) (ALL ENCLUSIVE GST @28% )
[ B] | Installation & Accessories
1 | Installation, charging and commissioning of the VRV systems with the R-410a refrigerant for the above stated machines as per the specs. This shall include the nitrogen leak testing, oil charging,vaccumisation and other accessories as per the specs- Gas Charging, Lifting Shifting etc. complete.
a | 12hp | Nos. | 1
2 | Installation, testing, commissioning indoor units mentioned in VRF equipment section during one calender year from date of hand over, including supply of indoor machine supports, fasteners (GI / SS), L/ angle iron frame if necessary for cassette.
a | ITC Of Indoor type VRF Units & DX Units for cassette | Nos. | 4
INDEGIOUS WORK.
3 | VRV Installation:
a | All refrigerant piping between indoor & outdoor units duly insulated. All piping inside the room shall be properly supported with hanger and exposed piping shall be properly supported. All piping shall be pressure tested for 1.5 times the working pressure.(Rate per meter will be for both length i.e, supply and returnrefrigerand pipes). | Rmt. | 55
b | 3 core x minimum 1.5 sq mm shielded Copper control cabling with saddles/ supports & PVC conduits to connect outdoor units with respective indoor units & remote controller units. Shield to be grounded on both ends for each circuit. | Rmt. | 80
c | Supply cabling to connect IDU power supply. Cables & accessories to be ISI marked. | Nos. | 4
4 | Supply & Installation of 1100V grade armoured cable having sector / circular shaped aluminium / copper conductor PVC insulated cores, laid up, PVC tape wrapped inner sheathed, GI strip / wire armoured and overall extruded PVC sheathed confirming to IS: 1554, laid on wall / ceiling using GI clamps & spacers or existing trench or to be laid in ground at 2' (feet) deep including excavation, Protective covering, & refilling the trench, excavated soil etc. to make the surface uniform with the existing ground lavel including the cost of all necessary hardwarw & accessories as per route shown at site and further as directed by Client / Consultant at site in the following sizes :-
a. | 4C x 16 Sq.mm Cu cable | Rmt. | 15
5 | END TERMINATION
Supply & Installation of end termination of above mentioned cables including compressed type brass glands, crimping type copper lugs, insulation tape etc. as 'required complete with earthing of glands in following (Suitable for Particular Cable Size)
a. | 4C x 16 Sq.mm Cu cable end termination | Nos. | 4
6 | Outdoor Stand
a | Supplying & Fixing of VRF Outdor Stand | Nos. | 1
7 | Drain Piping
a | Drain Piping shall be Hard 1" dia PVC for units drain Piping shall be insulated with 9mm Armaflex. | Rmt. | 75
TOTAL FOR INSTALLATION AMOUNT (B) (ALL ENCLUSIVE GST @18%)
GRAND TOTAL (A+B)
Note:-
1) All the rates shall be included of electricity supply & Water supply required for execution of work.
2) Exclusion: Any kind of civil works / carpentry works / temporary electrical supply / main electrical supply
3) All the Taxes shall be included all taxes.

## SUMMARY
INDIRA GANDHI INSTITUTE OF RESEARCH UP-GRADATION OF INFRASTRUCTURE FACILITIES
Summary for Supply, Installation & Commissioning of AC VRV System (Indoor & Outdoor Unit) Work at Guest House Conference. (Phase-3), in the campus.
SR NO. | ITEM | QUOTED AMOUNT (WITH GST)
1 | Interior Renovation of Guest House Conference AC VRV System Work
VRF system indoor and outdoor unit supply
Installation & accessories
Grand Total Amount
Say,